## Sheet1
Gateway Modbus address mapping for Mk5 controller
GA15_14 gen. 5 , BRP081379 | Mk5 controller must be in Mk5 CAN profile !
1900525735 - G/Z FS - Graphic 2.33.6.0 | Fixed Speed
16/03/2023 16:35:29
Coils
Name (1/0) | Coil
Running/Stopped | 1
Load/Unload | 2
General Warning | 3
General ShutdownWarning | 4
General Shutdown | 5
General Service | 6
General StartFailure | 7
Emergency Stop | 8
Automatic/Manual | 9
Remote/Local | 10
Analog Inputs |  |  | Registers
Name | Type | Unit | Status | Value | Value Interpretation
Saída do Compressor | Pressure (mBar) | mBar | 1 | 2 | Values are S16. 32767 = Sensor error.
Saída do Elemento | Temperature | 0.1 °C | 5 | 6
Ponto Orvalho do Secador | Temperature | 0.1 °C | 7 | 8
Digital Inputs |  |  | Registers
Name |  |  | Status | Value | Functional Interpretation 0/1
Parada de Emergência |  |  | 501 | 502 | Aberto / Fechado
Sobrecarga Motor/Ventilador |  |  | 503 | 504 | Aberto / Fechado
Partida/Parada Remota |  |  | 505 | 506 | Aberto / Fechado
Seleção do ajuste de pressão |  |  | 519 | 520 | Banda de Pressão 1 / Banda de Pressão 2
|  |  | Bit | Description (1/0)
|  |  | 0 | PreWarning
|  |  | 1 | Warning
|  |  | 2 | ShutdownWarning
|  |  | 3 | Shutdown
|  |  | 4 | Service
|  |  | 5 | Permissive
|  |  | 6 | Sensor Error
|  |  | 7 | Set/Not set
|  |  | 8 | SPM valid measurement
|  |  | 13 | PrePermissive
Digital Outputs |  |  | Registers
Name |  |  | Value |  | Functional Interpretation 0/1
Contator de Linha |  |  | 2551 |  | Aberto / Fechado
Contator Estrela |  |  | 2552 |  | Aberto / Fechado
Contator Triângulo |  |  | 2553 |  | Aberto / Fechado
Carga/Alívio |  |  | 2554 |  | Aberto / Fechado
Desligamento Geral |  |  | 2555 |  | Aberto / Fechado
Ligar Secador |  |  | 2556 |  | Aberto / Fechado
Operação Automática |  |  | 2557 |  | Aberto / Fechado
Aviso Geral |  |  | 2558 |  | Aberto / Fechado
Counters |  |  | Registers
Name |  | Unit | Value = (65536 x W2) + W1 |  | Reference counters for % calculation
|  |  | Value W2 | Value W1
Horas em Funcionamento |  | s | 1001 | 1002
Horas em Carga |  | s | 1003 | 1004
Núm. Partidas do Motor |  | Count | 1005 | 1006
Ciclos Carga/Alívio |  | Count | 1007 | 1008
Partidas do Secador |  | Count | 1009 | 1010
Horas do Modulo |  | s | 1013 | 1014
Special Alarms |  |  | Registers
Name |  |  | Status
Proteção do Secador Ponto de Orvalho |  |  | 2702
Controle de Pressão Inválido |  |  | 2703
Secador - Proteção Anti-congelamento |  |  | 2724
Comunicação - Módulo de Expansão |  |  | 2742
|  |  | Bit | Description (1/0)
|  |  | 0 | PreWarning
|  |  | 1 | Warning
|  |  | 3 | Shutdown
Machine Control Mode
Register 702 - LO byte
Name | Value
2a - Local Start/Stop & Pressure Sensing | 0
3a - Remote Start/Stop, Local Pressure Sensing | 1
4a - Communication Start/stop, Local Pressure Sensing | 2
2b - Local Start/Stop, Digital Contact Pressure Sensing | 16
3b - Remote Start/Stop, Digital Contact Pressure Sensing | 17
4b - Communication Start/Stop & SPS Control | 18
4c - Communication Start/Stop & Speed Control | 34
4d - ES/EQ Controlled | 50
2e - Local Start/Stop & 4-20mA Speed Control | 64
3e - Remote Start/Stop & 4-20mA Speed Control | 65
Machine Mechanical State
Register 701 - HI byte
Name | Value
Stop | 1
Unload | 2
Loaded | 4
General Status
Register 703
Name | Bit
PreWarning | 0
General Warning | 1
General Shutdown Warning | 2
General Shutdown | 3
General Service | 4
General Start Failure | 5
Emergency Stop | 6
Manual/Automatic | 7
Local/Remote | 8
Week Timer | 9
PreWarning Service Running Hours | 10
- | 11
PreWarning Service Analog Input | 12
PrePermissive | 13
Test Mode | 14
ESi/EQi Status
Register 709
Name | Value
PowerUp ES/EQ | 8209
Local Operation ES/EQ | 8225
Central Stop ES/EQ | 8242
Shutdown ES/EQ | 8337
Automatic Operation ES/EQ | 24594
ESi/EQi Counters |  |  | Registers
Name |  | Unit | Value = (65536 x W2) + W1
|  |  | Value W2 | Value W1
Compressor 1: Running Hours |  | s | 751 | 752
Regulation Parameters
Name | Register | Value Read | Value Write | Info
Pressure Band Selection | 861 | PB1=>1, PB2=>2 | PB1=>1, PB2=>2 | used in local pressure sensing mode
Pressure Band 1 - Load | 862 | mBar | n/a
Pressure Band 1 - Unload | 863 | mBar | n/a
Pressure Band 2 - Load | 864 | mBar | n/a
Pressure Band 2 - Unload | 865 | mBar | n/a
Actual used Load level | 866 | mBar | only for app 2.79 or higher and latest Gatewxay application | only for app 2.79 or higher and latest Gatewxay application
Actual used Unload level | 867 | mBar | only for app 2.79 or higher and latest Gatewxay application | only for app 2.79 or higher and latest Gatewxay application
ES(i) Pressure Band Selection | 881 | PB1=>1, PB2=>2 | PB1=>1, PB2=>2 | used in local pressure sensing mode
ES(i) Pressure Band 1 - Load | 882 | mBar | n/a
ES(i) Pressure Band 1 - UnLoad | 883 | mBar | n/a
ES(i) Pressure Band 2 - Load | 884 | mBar | n/a
ES(i) Pressure Band 2 - UnLoad | 885 | mBar | n/a
Info
External Set Point control | 871 | not applicable | MIN value =< value in 0.1°C =< MAX value
Commands - LAN mode
Name | Register | Value Read | Value Write | Info
Start | 2001 | n/a | 1 | Start the main machine
Stop | 2001 | n/a | 2 | Stop the main machine
Load | 2001 | n/a | 3
Unload | 2001 | n/a | 4